# Engineering Specification

# Model AAV Automatic Air Vent

Recommended CSI MasterFormat Specification Location: 21 13 13, Wet-Pipe Sprinkler Systems (formerly 13930)

A mechanical air purging device shall be [cULus Listed] [FM Approved] for wet-pipe sprinkler systems for vertical installation. The mechanical air vent shall automatically vent air from a high point in the system, and automatically close when water reaches the vent. The automatic air vent shall be constructed of a stainless-steel body with a ½” stainless steel screen with inspection port. The assembly shall have a working pressure rating of [175 psi (12.1 bar)] [300 psi (20.7 bar)].  The device shall be provided with a ½” NPT female inlet for connection to the system, and a ½” NPT male outlet connection for optional routing to drain.  The automatic air vent shall be the Reliable Model AAV. Refer to Reliable Bulletin 620 for associated information.