Engineering Specification

Model C Water Motor Gong

Water flow shall activate a mechanical, hydraulically powered water motor alarm through alarm line trim piping that does not exceed 75 feet in length or 20 feet in height above the alarm valve.  Water motor alarm shall be [cULus Listed] [FM Approved] [BS&A No. 587-75-SA] and shall automatically sound a continuous audible alarm when the sprinkler system operates.  Gong and motor housing shall consist of a bright metallic, red enameled, aluminum alloy.  Striker assembly shall be driven by a drive shaft connected to a pelton wheel.  Nylon non-lubricated bearings.  Water Motor Gong to be Reliable Model C, Bulletin 613.