# Engineering Specification

# Model D Dry-Pipe Valve

Recommended CSI MasterFormat Specification Location: 21 13 16, Dry-Pipe Sprinkler Systems (formerly 13935)

Dry-pipe valve shall be a [cULus Listed] [FM Approved] differential style clapper dry-pipe valve. Valve construction shall be cast iron utilizing a bronze seat and a ductile iron clapper assembly with a single hinge pin. Clapper gasket shall be a one-piece rubber design. Valve trim shall be galvanized. The dry-pipe valve shall be activated by a loss of supervisory pneumatic pressure based on a differential of six (6) to one (1) of the hydraulic pressure side versus the pneumatic pressure side, respectively. Supervisory pressure to be per the manufacturer’s published requirements. Dry-pipe valve shall have a rated working pressure of 175 psi (12.1 bar). Valve size shall be [4” (100 mm)] [6” (150 mm)] with flanged inlet by [grooved] [flanged] outlet. Flanged inlet [and outlet] shall be in accordance with ANSI B16.1 (125 lb). [Grooved outlet shall be per ANSI/AWWA C606.] [100 mm or 150 mm metric flanged inlet and outlet per EN 1092-2, NF-E-29-282, and BS 4504 PN 16 flanges.]

Dry-pipe valve shall be the Reliable Model D. Refer to Bulletin 350 for associated information.