# Engineering Specification

# Model F1FR56 QREC Series Quick Response Extended Coverage Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13930)

Sprinklers shall be a quick response, extended coverage [pendent] [horizontal sidewall] that is [cULus Listed] [FM Approved]. Sprinkler frame and deflector shall be of bronze frame construction having a ½” NPT thread.  Water seal assembly shall consist of a Teflon-coated Belleville spring washer and top-loaded extruded cup with 3 mm glass bulb containing no plastic parts. Sprinkler temperature rating shall be [135F (57C)] [155F (68C)] [SIN RA2865 only: 175F (79C)]. Sprinklers shall have a nominal K-factor of 5.6 gpm/psi1/2 (81 l/min/bar1/2) – standard orifice. Sprinklers shall have a rated working pressure of [175 psi (12 bar)] [SIN RA2845, UL Listed only: 250 psi (17 bar)]. Standard finish: [Bronze] [Chrome Plated] [White Polyester] [Special finish– specify].

Sprinklers shall be of the Model F1FR56 QREC Series. Refer to Reliable Bulletin 028 for associated sprinkler identification number (SIN) with respect to style, orifice size and thread combination.

For recessed pendent and/or horizontal sidewall sprinklers, add:

{Recessed escutcheon assembly shall be a factory-assembled, two-piece steel escutcheon of push-on and thread off design with ½” adjustment. Standard finish shall be [White Polyester] [Chrome Plated] [Brass] [special finish – specify].} {Recessed escutcheon assembly shall be a two-piece “friction fit” escutcheon with ½” adjustment. Standard finish: [White Polyester] [Chrome Plated] [Brass] [Special finish– specify].}

Recessed escutcheons that are listed for use with the Model F1FR56 QREC recessed pendent sprinkler shall be used.

For concealed pendent sprinklers, add:

Concealed pendent sprinklers shall have a factory-installed, steel sprinkler cup. Method of attaching the cover plate to the sprinkler cup shall be a push-on and thread-off design allowing [1/2” (13 mm)] [5/8” (8 mm)] of adjustment. The cover plate temperature rating shall be 135F (57C).  A factory applied protective cap shall be provided to protect against installation damage. Standard cover plate finish: [Chrome] [White] [Special finish– specify].

Cover plates used with the Model F1FR56 QREC concealed pendent shall be the Model CCP cover plate.