# Engineering Specification

# Model FX Dry-Pipe Valve

Recommended CSI MasterFormat Specification Location: 21 13 16, Dry-Pipe Sprinkler Systems (formerly 13935)

Dry-pipe valve shall be a [cULus Listed] [FM Approved] differential style clapper dry-pipe valve. Valve construction shall be ductile iron and utilize a stainless-steel seat and clapper assembly with a single hinge pin. Clapper gasket shall be integrated into the seat assembly and the valve trim shall be galvanized. Dry-pipe valve shall have an external reset feature and not require priming water. The dry-pipe valve shall be activated by a loss of supervisory pneumatic pressure based on a differential of six (6) to one (1) of the hydraulic pressure side versus the pneumatic pressure side, respectively. Supervisory pressure to be per the manufacturer’s published requirements. Dry-pipe valve shall have a rated working pressure of [for 2” valve: 250 psi (17.2 bar)] [300 psi (20.7)]. Valve size shall be [2” (50mm)] [2½” (65mm)] [76mm] [3” (80mm)] [4” (100mm)] {cULus Listed only: [6” (150 mm)] [165 mm]} with [Groove/Groove] {for 4” and 6” valves only: [Flange/Groove] [Flange/Flange]} end connections. {Flanged end connections shall be in accordance with [ANSI B16.1 (125 lb)] [BS10 BS-E] [ISO 7005-2 PN16].} [Grooved end connections shall be per ANSI/AWWA C606.]

Dry-pipe valve shall be the Reliable Model FX. Refer to Bulletin 360 for associated information.