# Engineering Specification

# Model G6-80 Series Quick Response Extended Coverage

# Light Hazard Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 13, Wet Pipe Sprinkler Systems (formerly 13930)

Sprinklers shall be quick-response extended coverage flat concealed horizontal sidewall sprinklers that are cULus Listed for use in Light Hazard occupancies. Sprinklers to be of bronze frame construction with brass cover plate and copper alloy retainer flange assembly. Water seal assembly shall consist of a PTFE coated Belleville spring washer and machined brass cup containing no plastic parts. Method of attaching the cover plate to the sprinkler cup shall be a push-on and pull-off design allowing a ¼” (6 mm) cover plate adjustment. Sprinklers shall have a nominal K-factor of 8.0 gpm/psi1/2 (115 l/min/bar1/2) and [¾” NPT] [ISO 7-R¾] thread. Sprinkler temperature rating shall be 165°F (74°C) with a cover plate temperature rating of 135°F (57°C). Sprinklers shall be capable of a maximum coverage area of [16 ft. x 24 ft. (4.9 m x 7.4 m)] [18 ft. x 22 ft (5.5 m x 6.7 m)], with a minimum lateral spacing of 8 ft. (2.4 m). Rated working pressure shall be 175 psi (12 bar). A plastic protective cap shall be provided and factory installed inside the sprinkler cup to protect the sprinkler from damage, which could occur during construction before the cover plate is installed. Standard cover plate finish: [White] [Chrome] [Custom Finish – specify].

Flat concealed quick-response extended coverage horizontal sidewall sprinklers shall be Reliable Model G6-80, SIN RA4762, Reliable Bulletin 047.