# Engineering Specification

# Model GFR Quick Response Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13930)

Sprinklers shall be a quick response [standard spray upright] [standard spray pendent] [conventional upright/pendent] that is [cULus Listed] [FM Approved] [MIL-S-901C and MIL-STD-167-1]. Sprinkler frame and deflector shall be of bronze frame construction having a [½”] [¾”] NPT thread.  Water seal assembly shall consist of an approved painted beryllium-nickel fusible solder link assembly, utilizing a strut and lever principal of operation, with Teflon-coated copper alloy cap containing no plastic parts.  Sprinkler temperature rating shall be [165 F (74 C)] [212F (100 C)]. Sprinklers shall have a nominal K-factor of [2.8 gpm/psi1/2 (40.6 l/min/bar1/2) – small orifice] [4.2 gpm/psi1/2 (61 l/min/bar1/2) – small orifice] [5.6 gpm/psi1/2 (81 l/min/bar1/2) – standard orifice] [8.0 gpm/psi1/2 (115 l/min/bar1/2) – large orifice]. Small orifice sprinklers shall be used in wet pipe systems and light hazard occupancies only. Sprinklers shall have a rated working pressure of 175 psi (12.1 bar).  Standard finish shall be [Bronze] [Chrome plated] [Special finish– specify].

Sprinklers shall be of the Model GFR Series. Refer to Reliable Bulletin 131 for associated sprinkler identification number (SIN) with respect to style, orifice and thread combination.

## For recessed pendent and/or recessed horizontal sidewalls, add:

{Recessed escutcheon assembly shall be a factory-assembled, two-piece steel escutcheon of push-on and thread off design with ½” adjustment. Standard finish shall be [White Polyester] [Chrome Plated] [Brass] [special finish – specify].} {Recessed escutcheon assembly shall be a two-piece “friction fit” escutcheon with ½” adjustment. Standard finish: [White Polyester] [Chrome Plated] [Brass] [Special finish– specify].} Recessed escutcheons that are permitted to be used with each Model GFR Series recessed sprinkler shall be used.