# Engineering Specification

# Model KRes Series Horizontal Sidewall Fusible Link

# Residential Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 13, Wet-pipe Sprinkler Systems (formerly 13930)

Sprinklers shall be residential type cULus Listed for installation in accordance with NFPA 13, NFPA 13R, and NFPA 13D. Residential sprinklers shall be installed in conformance with the manufacturer’s installation guidelines and the applicable installation standard. Sprinkler body shall be of bronze alloy construction having [½” NPT] [ISO7-1R1/2] threads.  Sealing assembly shall be nickel alloy with PTFE. Thermal element shall be a nickel alloy fusible link.

KRes44 and KRes58

Sprinkler shall be UL listed for coverage areas up to 16’x20’ utilizing a K-factor of [4.4 gpm/psi1/2 (63 l/min/bar1/2)] [5.8 gpm/psi1/2 (84 l/min/bar1/2)]. Sprinkler temperature classification shall be [Ordinary 165F (74C)]. Finish to be [brass] [white] [chrome] [special – specify].

For recessed sprinklers, add:

Recessed Horizontal sidewall sprinklers shall be installed with listed 2-piece escutcheons offering a minimum of ½” (12.7mm) adjustment. Sprinkler deflector to be located between 4” and 12” below the ceiling. Escutcheon color to be [brass] [white] [chrome] [special – specify] consistent with sprinkler finish.

Residential Horizontal Sidewall sprinklers shall be Reliable Model [KRes44, SIN RA3591] [KRes58, SIN RA3503].

KRes58 HSWX

Sprinkler shall be UL listed for coverage areas up to 14’x26’ utilizing a K-factor of 5.8 gpm/psi1/2 (84 l/min/bar1/2). Sprinkler temperature classification shall be [Ordinary 165F (74C)]. Finish to be [brass] [white] [chrome] [special – specify].

For recessed sprinklers, add:

Recessed Horizontal sidewall sprinklers shall be installed with listed 2-piece escutcheons offering a minimum of ½” (12.7mm) adjustment. Sprinkler deflector to be located between 4” and 12” below the ceiling. Escutcheon color to be [brass] [white] [chrome] [special – specify] consistent with sprinkler finish.

Residential Horizontal Sidewall sprinklers shall be Reliable Model KRes58 HSWX, SIN RA3593.