# Engineering Specification

# Model MBEC-14 Extended Coverage

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13900)

Sprinklers shall be a specific application extended coverage sprinkler, Model MBEC-14, that is [cULus Listed] [FM Approved] specifically for the protection of metal buildings with purlin roof support. Sprinkler frame and deflector shall be of bronze frame construction having a 3/4” NPT  thread.  Water seal assembly shall consist of an approved beryllium-nickel fusible solder link assembly, utilizing a strut and lever principal of operation, with PTFE-coated nickel sealing washer and bronze alloy cap containing no plastic parts.  Sprinkler temperature rating shall be [165F (74C)] [212F (100C)]. Sprinklers shall have a nominal K-factor of 14.0 gpm/psi1/2 (200 l/min/bar1/2) – very extro large orifice. Sprinklers shall have a rated working pressure of 175 psi (12 bar).  Finish shall be [Bronze] [Chrome].

Sprinklers shall be Reliable Model MBEC-14, SIN R6932. Refer to Reliable Technical Bulletin 169 for associated sprinkler information.