# Engineering Specification

# Model XL Flush Series Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13900)

Sprinklers shall be flush style, UL Listed quick response [pendent] [horizontal sidewall].  Sprinkler and deflector to be of bronze construction with ½” NPT thread. Levered fusible solder link shall consist of an approved black-painted beryllium-nickel link assembly. Water seal shall consist of a Teflon-coated Bellville spring washer and bronze diffuser sub-assembly containing no plastic parts. Sprinkler K-factor shall be nominal 5.6 gpm/psi1/2 (81.0 l/min/bar1/2). Sprinkler temperature rating shall be Ordinary 165F (74C). Sprinklers shall have a rated working pressure of 175 psi (12.1 bar). {Pendent escutcheon style shall be [Conical, capable of providing 3/16” (5 mm) of adjustment] [Flat, capable of providing 3/16” (5 mm) of adjustment]} {Horizontal sidewall escutcheon style shall be conical, capable of providing 5/16” (8 mm) of adjustment.}  Standard cover finish shall be [Bright Chrome Plated] [Dull Chrome Plated] [White Painted] [Special finish – specify].

Sprinklers shall of the Model XL Flush Series, [Commercial Pendent, SIN R5414] [Commercial Horizontal Sidewall, SIN R4534]. Refer to Reliable Bulletin 145 for associated sprinkler information.