# Engineering Specification

# Model XL Institutional Sprinkler

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13900)

Institutional sprinklers shall be cULus Listed quick response, [pendent, standard coverage sprinklers] [horizontal sidewall sprinklers, standard coverage] [pendent, extended coverage] [horizontal sidewall, extended coverage]. Sprinkler and deflector to be of bronze construction, with ½” NPT thread. Levered fusible solder link shall consist of an approved black-painted beryllium-nickel link assembly.  Fusible link shall be designed to release a suspended load that exceeds 50 lbs. (22.7 kg) when dropped from a 1-inch (25.4 mm) height. Water seal shall consist of a PTFE-coated Bellville spring washer and bronze diffuser sub-assembly containing no plastic parts. Institutional escutcheons shall be of zinc or aluminum construction with zinc ring plate and tamper resistant screws.  Sprinkler K-factor shall be nominal 5.6 gpm/psi1/2 (81.0 l/min/bar1/2) – standard orifice. Sprinkler temperature rating shall be 165 F (74 C).  Sprinklers shall have a rated working pressure of 175 psi (12 bar).  Standard cover finish: [Bright chrome plated] [Specialty – specify].

Sprinklers shall be Reliable Model XL Institutional [Pendent, Standard Coverage, SIN R1314] [Pendent, Extended Coverage, SIN R1344] [Horizontal Sidewall, Standard Coverage, SIN R1334] [Horizontal Sidewall, Extended Coverage, SIN R1364]. Refer to Reliable Technical Bulletin 113 for associated sprinkler information.